# Load Flow Studies

# Introduction

In this section, we are looking at how can we analyze the power system in steady state in normal operation. In steady state, the state variables that describe the system doesn’t diverge from its normal operating point and remain constant. For the analysis associated with this section we assume the following

Network equations can be formed for all the network elements. From circuit analysis knowledge, the node voltage method can be used to analyze a circuit.

Example: Analyze the below circuit with node voltage method

Figure 1. Example circuit for node voltage analysis

It can be seen that when the equations are written with node current injections, solving the circuit resolves into complex linear set of simultaneous equations. Node voltages can be easily solved after obtaining the inverse of the admittance matrix.

Example:

Consider the following problems:

1. V2, δ2 , P2 and Q2 are given. Find V1, δ1 , P1 and Q1.

2. V1, δ1 , V2 and δ2 are given. Find P1, Q1 , P2 and Q2.

3. P2, Q2 , V1 and δ1 are given. Find V2, δ2 , P1 and Q1.

However, in power system usually the node active power and reactive power injections are specified, rather than current injections. Thus the resulting equations based on power are defined as “power flow equations” or “load flow equations”. These two terms are used interchangeably in the literature.

Apparent power S=VI*, which is a nonlinear equation. This makes the above power flow equations non-linear. These non-linear equations cannot be easily solved as algebraic equations and require iterative solution methods.

Solving for the power flow of a network gives the node (or bus) voltages and angles, active and reactive power flow in branches (transmission lines and transformers). These information is essential for

- Power system planning and design

- Planning

- Operation

- Economic scheduling

- Contingency studies

- Calculate initial conditions for transient stability and Electromagnetic transient simulation studies.

This section is aiming to cover the following sections

- Mathematical formulation of load flow studies.

- Different solution techniques to solve the non-linear load flow equations

# Mathematical Formulation

## Bus Admittance Matrix

Let us expand the node voltage analysis in previous section to a simple power system with two generators (voltage source behind a reactance) and four branches made with reactance (resistance and shunt capacitance are neglected for simplicity).

Figure 2. Example simple power system with impedances.

Node voltage method is based on Kirchoff’s current law → easy to analyze with admittances rather than impedance

yij=1zij=1rij+jxij

Redraw circuit with admittances and voltage sources by their respective Norton equivalent current sources

Figure 3. Redrawn circuit with admittance and current sources.

Applying KCL for each node and re arranging the terms as done in previous section

Arranging in matrix form

In the above equation Ibus is the vector of bus current injections (positive if current is injected to the bus) and is complex in general. Vbus is the bus voltage vector and is complex in general. Ybus is the bus admittance matrix and its elements are generally denoted as Yij where i is the row number and j is the column number. Diagonal elements of Ybus are known as driving point admittance or self-admittance and is the addition of all the admittances connected to the node of interest.

Yii=j=0nyij                                j≠ⅈ

Off diagonal elements equal to the negative admittances between the two nodes (busses) represented by row and column numbers. This element is known as mutual admittance or transfer admittance.

Yij=Yji=-yij

Solution of the voltages

Vbus=Ybus-1Ibus

Inverse of admittance matrix Ybus-1 is bus impedance matrix. If the admittance matrix is defined with a reference bus (slack bus which is described later) the matrix is non-singular. Otherwise the matrix is singular.

Admittance matrix is symmetrical around the leading diagonal. Thus only requires to store information on half of the matrix. This is important when considering real size grids containing thousands of busses. (Typical power system analysis of North American eastern Interconnection is modelled with around 70,000-80,000 busses).

Typically admittance matrix is sparse. Usually correctly ordered triangular decomposition methods are used to calculate the inverse of such large sparse matrices gaining computational speed (students are advised to read on the mathematics for more information).

## Load Flow/Power Flow Equation

Load flow solution solves for bus voltages (magnitude and angle) and active and reactive power flows in the branches. Four quantities are associated with each bus

- Voltage magnitude V

- Voltage angle δ

- Active (real) power P

- Reactive power Q

Busses of the power system are categorized into three main types based on how they are operated

- Slack Bus/ Swing Bus

- PV busses/ Generator busses / Regulated busses

- Load busses/ PQ busses

Consider a bus in a network as shown below.

Figure 4. Bus i of the power system connected to n number of busses.

- Obtain an expression for bus current injection.

- Write an expression for apparent power using voltage and current.

- Substitute for the current.

Thus we observe the equation is non-linear and we have to resolve for iterative methods to solve the equation. In the next section we will first look at few non-linear algebraic equation solution methods in general. Then we could apply the iterative methods to solve for the load flow equations.

# Solving Non-linear Algebraic Equations

Different iterative calculation methods are used to solve non-linear algebraic equations.

- Gauss-Seidel Method

- Newton-Raphson Method

- Quasi-Newton Methods

First, the general concept of these methods are discussed for one-dimensional and n-dimensional equations. Then they are extended to solve the non-linear equations in in power flow equations.

## Gauss-Seidel Method

Method is also known as successive displacement.  Consider the solution of the following non-linear equation.

fx=0

The equation can be re-arranged as follows

x=gx

Lets say the initial estimate of x is x(k). Then we can form the following iterative sequence

xk+1=gxk

A solution is obtained when the difference between successive iterations are less than a specified accuracy

xk+1-xk≤ϵ

Example: Use Gauss-Seidel method to find the root of the following equation.

fx=x3-6x2+9x-4=0

Solution:

Re arrange the equation as follows

x=-19x3+69x2+49

x=gx

We can plot x and  gx over a range of x values as follows. The solution will be the x values where the two curves intersect.

The figure shows that there are roots existing at x=1, and x=4.

Ex: Calculate three iterations of the Gauss-Siedel algorithm

Figure 5. Progression of estimate of x in Gauss-Seidel algorithm.

Figure 6. Process of solution of Gauss-Seidel method

Considerable number of iterations were taken to reach the solution. The convergence of the solution is not guaranteed as well.

To make the convergence of the solution faster, an acceleration factor (α) can be introduced to the Gauss-Seidel algorithm.

xk+1=xk+αgxk-xk

In a system of n non-linear equations with n variables

f1x1,x2,…,xn=c1

f2x1,x2,…,xn=c2

⋯

fnx1,x2,…,xn=cn

Rearranged as follows

x1=c1+g1x1,x2,…,xn

x2=c2+g2x1,x2,…,xn

⋯

xn=cn+gnx1,x2,…,xn

The algorithm is initiated with initial estimates for the n variables. (x1(0),x2(0),…,xn(0)). The initial estimates are used in the first non-linear equation and the calculated variable from first equation is used in subsequent equations. This is carried out for all the non-linear equations. The accuracy of each variable is tested for all variables in each iteration. The algorithm is converged when all variables successive calculated values are within the specified tolerance.

## Newton-Raphson Method

This is the most used algorithm for solving non-linear algebraic equations. The method relies on successive approximation based on initial estimate.

Consider the one dimensional equation

fx=c

If x(0) is the initial estimate and ∆x(0) a small perturbation from the solution

fx(0)+ ∆x(0)=c

Expand the left hand by Taylor’s series expansion

fx0+ⅆfⅆx0Δx0+12!ⅆ2fⅆx20Δx02+⋯=c

It can be assumed that the perturbation is very small making the higher order terms negligible

ⅆfⅆx0Δx0≈c-fx0=Δc(0)

The second approximation is derived by adding the Δx0 term to the initial estimate

x1=x0+Δc0ⅆfⅆx0

This procedure can be iteratively used to approximate the solution, and thus Newton-Raphson algorithm is developed. For generally the kth iteration:

Δck=c-fxk

Δxk=Δckⅆfⅆxk

xk+1=xk+Δxk

This can be rearranged as

Δck=jkΔxk

Where

jk=ⅆfⅆxk

Newton-Raphson method effectively construct the tangent at the first estimate value, and find the intersection of tangent line with c curve. The new estimate for x is obtained at the intersecting point.

Example: Use Newton-Raphson method to find the root of the following equation.

fx=x3-6x2+9x-4=0

Solution:

Figure 7. Plot of f(x)

Next following results

| Iteration (k) | Δck | ⅆfⅆxk | Δxk | xk+1 |
| --- | --- | --- | --- | --- |
| 1 | -13.443 | 22.037 | -0.610 | 4.278 |
| 2 | -2.998 | 12.579 | -0.238 | 4.040 |
| 3 | -0.374 | 9.491 | -0.039 | 4.001 |

Figure 8. Progression of the estimates of x in Newton Raphson method.

It can be seen that the convergence is faster than Gauss-Seidel method. It can be seen that the iterative methods can converge at a different root, if the initial estimate is far from the expected root (solution).

Figure 9. Progression of Newton-Raphson method with initial estimate at -1.0.

For an n dimensional set of equations with n variables, where perturbations are expanded using Taylor’s series and neglecting higher order terms as done for one-dimensional derivation

f10+∂f1∂x10Δx10+∂f1∂x20Δx20+…+∂f1∂xn0Δxn0=c1

f20+∂f2∂x10Δx10+∂f2∂x20Δx20+…+∂f2∂xn0Δxn0=c2

⋯

fn0+∂fn∂x10Δx10+∂fn∂x20Δx20+…+∂fn∂xn0Δxn0=c2

Or in matrix form

c1-f10c2-f20⋮cn-fn0=∂f1∂x10∂f1∂x20⋯∂f1∂xn0∂f2∂x10∂f2∂x20⋯∂f2∂xn0⋮⋮⋱⋮∂fn∂x10∂fn∂x20⋯∂fn∂xn0Δx10Δx20⋮Δxn0

Or in short matrix symbols it can be re-written

ΔCk=JkΔXk

Or

ΔXk=Jk-1ΔCk

Newton-Raphson algorithm for the next estimate becomes

Xk+1=Xk+ΔXk

Jk is known as the Jacobian matrix. This matrix is formulated with partial derivatives of the set of equations at the estimated value. During the Newton-Raphson calculation, it is assumed that the Jacobian matrix is non-singular.

## Using Gauss-Seidel Algorithm to Solve the Load Flow Equation

The load flow equation for voltage modified for Gauss-Seidel algorithm is as follows

Vik+1=Pisch-jQischVi*(k)+∑yijVjk∑yij         j≠i

The load flow equations were developed assuming currents are injecting into the bus. Therefore, for loads active Pisch and reactive (inductive reactive) Qisch power flows will be negative. For generators which inject active and reactive power into the bus Pisch and Qisch will be positive.

Pik+1=ReVi*(k)Vikj=0nyij-j=1nyijVjk         j≠i

Qik+1=-ImVi*(k)Vikj=0nyij-j=1nyijVjk         j≠i

Representing the equations with elements in Ybus bus admittance matrix

Voltage equation:

Active power equation:

Reactive power equation:

### Solving for load busses/PQ busses

For PQ busses, both  Pisch and Qisch are known and voltage magnitude and phase angle are unknown. Thus the above voltage equation is used to solve for the real and imaginary components of the voltage. Thus for each PQ bus, two equations are solved (real and imaginary).

### Solving for generator busses/PV busses

Generator busses have Pisch and Vi are specified. The initial estimate of the voltages are used to first evaluate the reactive power schedule Qisch at the bus using the above reactive power equation. Then a voltage estimate for the bus is calculated using the voltage equation.

Vi,estk+1=

However the voltage magnitude of the PV bus is constant and specified in the problem. Thus the real part of the final voltage estimate is obtained such that

Vⅈk+1=

For a power system in normal operating region, the bus voltages are in the neighborhood of 1.0 pu or closer to the slack bus. Bus voltage magnitude and angles change depending on the active and reactive power flow through the system. Thus a initial estimate of 1.0+j0.0 pu is satisfactory for most of the power systems.

In Gauss-Seidel algorithm, the updated voltages replace the previous values for subsequent equations.

The algorithm can be made faster by using an appropriate acceleration factor as shown below.

Vik+1=Vik+αVⅈ,ⅇstk-Vik
 The iterative process is carried out until the difference between successive iterations in both real and imaginary components are within a specified accuracy ϵ. In order to get reasonable power mismatch, very tight tolerances need to be specified (0.00001-0.00005 pu)

ReVⅈk+1-ReVⅈk≤ϵ

ImVⅈk+1-ImVⅈk≤ϵ

## Using Newton-Raphson Algorithm to Solve the Load Flow Equation

Ex. Obtain an expression for active power and reactive power injected into a bus i in a n bus system.

For PQ busses, there will be two equations for both active and reactive power. For PV busses, there will be one equation for active power (since reactive power is not set)

Taking bus number 1 as the slack bus and expanding the above two equations using Taylor’s series expansion around the initial estimate, and neglecting higher order terms

∆P2(k)⋮∆Pn(k)∆Q2(k)⋮∆Qn(k)=∂P2∂δ2(k)⋯∂P2∂δn(k)∂P2∂V2(k)⋯∂P2∂Vn(k)⋮⋱⋮⋮⋱⋮∂Pn∂δ2(k)⋯∂Pn∂δn(k)∂Pn∂V2(k)⋯∂Pn∂Vn(k)∂Q2∂δ2(k)⋯∂Q2∂δn(k)∂Q2∂V2(k)⋯∂Q2∂Vn(k)⋮⋱⋮⋮⋱⋮∂Qn∂δ2(k)⋯∂Qn∂δn(k)∂Qn∂V2(k)⋯∂Qn∂Vn(k)∆δ2(k)⋮∆δn(k)∆V2(k)⋮∆Vn(k)

The Jacobian matrix gives relationships between small changes in voltage angle and voltage magnitude to small changes in active and reactive power.

ΔPΔQ=J1J2J3J4ΔδΔV

### Order of the Jacobian matrix

For a power system with n busses, there is one slack bus

For PQ busses, both active power and reactive power constraints exists.

For PV busses, the bus voltage magnitude is controlled and thus equations involving ∆Q and ∆V and the corresponding columns are eliminated.

Thus there will be n-1 active power constraint equations and if there are m number of PV busses, n-1-m reactive power constraint equations will exist.

J1  matrix is of order n-1×n-1

J2  matrix is of order n-1×n-1-m

J3  matrix is of order n-1-m×n-1

J4  matrix is of order n-1-m×n-1-m

Thus the order of the Jacobian is 2n-2-m×2n-2-m

### Elements of the Jacobian matrix

For completion, the element of the Jacobian matrix is presented here. It is advised to derive these expressions on your own for familiarity.

J1  matrix

Diagonal elements	 ∂Pi∂δi=j≠iViVjYijsinθij-δi+δj

Off-diagonal elements	 ∂Pi∂δj=-ViVjYijsinθij-δi+δj      j≠i

J2  matrix

Diagonal elements	 ∂Pi∂Vi=2ViYiicosθii+j≠iVjYijcosθij-δi+δj

Off-diagonal elements	∂Pi∂Vj=ViYijcosθij-δi+δj           j≠ⅈ

J3  matrix

Diagonal elements	 ∂Qi∂δi=j≠iViVjYijcosθij-δi+δj

Off-diagonal elements	∂Qi∂δj=-ViVjYijcosθij-δi+δj                 j≠ⅈ

J4  matrix

Diagonal elements	 ∂Qi∂Vi=-2ViYiisinθii-j≠iVjYijsinθij-δi+δj

Off-diagonal elements	∂Qi∂Vj=-ViYijsinθij-δi+δj            j≠ⅈ

### Power residuals

Difference between the scheduled and calculated values

ΔPik=Pisch-Pik

ΔQik=Qisch-Qik

New estimates of voltages

δik+1=δik+Δδik

Vik+1=Vik+ΔVik

### Procedure of conducting load flow calculation using Newton-Raphson method

Step 1

- PQ bus, Pisch and Qisch are specified. Initial voltage magnitudes and angles set to equal slack bus

- PV bus  Pisch and Vi are specified. Phase angle set to equal slack bus

Step 2

- For PQ busses, Pik and Qik are calculated

- ΔPik and ΔQik calculated

Step 3

- For PV busses, Pik and ΔPik are calculated.

Step 4

- For the current iteration estimates, Jacobian matrix is calculated.

Step 5

- The following equation is solved for the current estimates to obtain changes in phase angle and voltage magnitude

ΔPΔQ=J1J2J3J4ΔδΔV

Step 6

- New voltage magnitudes and angles are calculated

δik+1=δik+Δδik

Vik+1=Vik+ΔVik

Step 7

- The process is continued until

ΔPik≤ϵ

ΔQik≤ϵ

## Using Fast Decoupled Algorithm to Solve the Load Flow Equation

Transmission lined in the power system are more inductive than resistive. Thus the X/R ratio is very high, and the real power change due to the voltage magnitude change is less sensitive and most sensitive to changes in voltage angle.

Similarly, reactive power change is less sensitive voltage angle, but most sensitive to changes in voltage magnitude.

Thus the following simplification can be done

ΔPΔQ=J100J4ΔδΔV

Or

ΔP=J1Δδ=∂P∂δΔδ

ΔQ=J4ΔV=∂Q∂VΔV

This shows that the larger Jacobian matrix has now been decoupled into two equations with smaller matrix order.

Further simplifications can be made to J1 and J4 in order to eliminate the need of recomputing the two matrices.

J1  matrix simplification

J4  matrix simplification

In the above equations B' and B'' are the imaginary part of the bus admittance matrix.

Fast decoupled method requires more iterations than Newton Raphson method, but each iteration requires less computation time. To solve for voltage magnitude and angle, the inverse of B' and B''needs to be calculated, but it is only required to calculate once for load flow solution.

# Tap Changing Transformer in Power Flow Calculation

Tap changing transformers are used in the power system to control active and reactive power transfer. The tap ratio (ratio of the voltage against the nominal ratio) is complex for phase shifting transformers.

Consider a tap changing transformer shown below. The transformer admittance is represented by yt (in pu) and the off-nominal transformer tap ratio (1:a, a is per unit tap position) is presented by an ideal transformer.

Figure 10. Tap changing transformer model.

Complex power on both sides of the ideal transformer are the same. Thus

Vx=1aVj

Ii=-a*Ij

But the current on i end

Ii=ytVi-Vx

Ii=ytVi-ytaVj

Substituting for Ii

Ij=-yta*Vi+yta2Vj

Writing equations for Ii and Ij in matrix form

IiIj=yt-yta-yta*yta2ViVj

Figure 11. Tap changing transformer equivalent network